## ADRESSING
Q. No | Type | Question | A | B | C | D | Correct Answer
|  | What is meant by QB and QW ? | quality bit & quality word | Terms used in PLC | Output Byte and Output Word. | None of the above | c
|  | What range of inputs IW 0 covers ? . | I 0.0 to I 0.7 | I 0.0 only | I 0.0 to I 1.7 | None of the above | c
|  | Can an analog signal be read direct from the Analog address in Siemens PLC | Yes | No | Can't say | None of the above | a
|  | Which the following is not downloaded to PLC in case of S7 controllers? | Organization Block | Symbols Table | Data Blocks | Function Block | b
|  | Any change in symbol is updated in which table | Force table | Symbol table | VAT table | None | b
|  | The following is used to send data from PLC to HMI | Graphics | smart objects | Tags | Trends | c
|  | What will be the maximum value of any analog input in case of a 12 bit AI module? | 4095 | 4096 | 2048 | 2046 | a

## COMMUNICATION
Q. No | Type | Question | A | B | C | D | Correct Answer
|  | By default, the baud rate of MPI Communication is____________________ | 125 Kbps | 152.5 Kbps | 187.5 Kbps | 215 Kbps | c
|  | DP stands for_______________________ | Distributed Port | Distributed Periphery | Direct Periphery | Dual Periphery | b
|  | Which of the following has the maximum speed ? | PROFIBUS DP | MPI | ETHERNET | All | c
|  | Default speed of PROFIBUS network is : | 1.5 Mbps | 187.5 kbps | 257 kbps | 6 Mbps | a
|  | Profibus DP connector is a 9 Pin SUB D type connector | True | False |  |  | a
|  | Profibus DP works on RS 232 and Profibus PA work on RS 485 | True | False |  |  | b
|  | The following is used to enhance signal strength of profibus n/w | Amplifier | Repeater | Connector | Profitrace | b
|  | Transfer medium used for Profibus DP system can be | Shielded twisted two wire cable | Glass or plastic fiber optic cable | Both of the above | None | c
|  | IM module is used to keep a high transmission rate on DP network when a large no. of devices are connected to the network | True | False | Any | None | a
|  | You need to power the DP instruments, while PA instruments get its power and exchange data via the same PA cable . | True | False |  |  | a

## HARDWARE
Q. No | Type | Question | A | B | C | D | Correct Answer
|  | Which one of this is a Siemens Software | RSView | RSLogix | Wincc | RSNetworx | c
|  | Can CPU be mounted on Extension rack? | Yes | No | Cannot be said |  | b
|  | What is the maximum number of slots possible in any S7 rack? | 9 | 15 | 18 | 22 | c
|  | Hardware configuration is saved in the form of _______________ | SDB | SFC | DB | SFB. | a
|  | Interface module of S7 300 PLC is placed on slot no _____ | 2 | 3 | 11 | 9 | b
|  | When PLC S7 400 is restarted which of the following action takes place | Cold Restart | Warm Restart | Hot Restart | As selected by the user. | d
|  | Analog I/O and Digital I/O come under which category of modules? | Interface Module | Signal Module | CPU | All of the above | b
|  | In which mode CPU should be put for saving the Project in Flash Memory? | RUN-P | RUN | STOP | In any mode | c
|  | Which software is used to write a program in Siemens PLC? | RS logix | Simatic Manager | Control Builder | PL7 | b
|  | Which of the following is not a type of SIMENS PLC | S7 - 200 | S7 - 300 | S7- 400 | S7- 500 | d
|  | S-7 PLC is | Allen bradly PLC | GE PLC | Siemens PLC | Fanuc PLC | c
|  | The following is the software for programming siemens PLC | Step 7 | Wincc | Siwatool | Ultra VNC | a
|  | While configuring the PLC which is the first unit configured ? | rack | power supply | CPU | None of the above | a
|  | RAM Memory back up battery is placed in | CPU Module | Power supply Module | I/O Module | communication Module | b
|  | RAM Backup Battery should be removed only under the condition | CPU Power Off | CPU Power ON | Both | None | b
|  | Total types of racks in Siemens PLC SIMATIC S7-400 are ____. | 2 | 3 | 4 | 6 | b
|  | In Siemens PLC SIMATIC S7-400 , ER has ____ bus. | P bus only | K bus only | both P bus & K bus | none of these | a
|  | What is placed in the first slot in main rack in Siemens PLC SIMATIC S7-300/400 ? | Communication processor | Power supply | CPU | Signal module | b
|  | Which module is used in siemens plc to measure the High Speed encoder pulses in plc | Function Module | Analog Module | Digital Module | None | a
|  | IP addresses are assigned to __________ module | Profibus Module | I/O Module | Processor Module | All of the above | c
|  | The communication between PLC and field devices rack is done using | Ethernet | Profibus | Wireless | Coaxial cable | b
|  | The port used for profibus communication with PLC is | MPI | DP | RS232 | Lan port | b
|  | The redundant PLCs communicate with each other via | Ethernet | Profibus | Wireless | FO cable | d
|  | In a hot stand by system, both of the controller racks should have | Same type of Rack | Same type of communication processor | Same type of controllers | All modules Identical | d
|  | PS407,10A occupies ________ slots in the rack | 1 | 2 | 3 | 4 | b
|  | Which CP is used for communication over Industrial Ethernet protocol | CP443-1 | CP443-5 | CP441-1 | CP441-5 | a
|  | Which of the following is a part of system memory | Input Image Table | Timers & Counters | Diagonostic Buffer | All of the above | d
|  | The default watch dog time in Siemens PLC is | 50 ms | 100 ms | 150 ms | 500 ms | c
|  | Entire program of the PLC is stored in | Work Memory | Load Memory | System Memory | None | b
|  | Which of the following is not a function of input modules | Interfacing of field devices with PLC | Conversion of the field level signal to CPU level signal. | Isolation of field inputs from the controller | Maintaining the status of signal till next input scan | d
|  | IEC 61131 is an IEC Standard for | Profibus Comm | Programmable Logic Controller | Ethernet Comm | None | b
|  | Two different PLCs can be configured with the same node address on a network. | True | False | It depends on type of PLC | None of the above | b

## INSTRUCTIONS
Q. No | Type | Question | A | B | C | D | Correct Answer
|  | In SR Flip Flop of S7, output (Q) is set when | If S = 1 and R = 0 | If S = 0 and R = 1 | If S = 1 and R = 1 | Both option a and c | a
|  | What is the maximum value the Preset Value of a S7 counter can take ? | 900 | 990 | 999 | 1000 | c
|  | Name a timer which when made ON can only be turned OFF by activating the RESET bit- | On Delay Timer | Off Delay Timer | Extended Pulse Timer | Set Storage Timer | d
|  | S7 counter output is high when | counter value is = preset. | counter value is < preset. | counter value is > preset. | counter value > 0 | d
|  | How many types of timers are present in PLC S-7 400 | 2 | 4 | 3 | 5 | d
|  | Maximum time delay that can be achieved through an S7 timer is- | 9999 sec | 9990 sec | 999 sec | 990 sec | b
|  | The format for time input in any timer in S-7 400 PLC is______________. | S5T*<time> | S5T%<time> | S5T#<time> | L KT 10.0 | c
|  | Which operator can be used to place two or more output coils in series in the same network? | Save | Reset coil | Midline output | All the above. | c
|  | What is the data type of S input in S7 timer? | Boolean | Word | Double word | String | a
|  | When does the output of an S7 counter become high? | Counter value is equal to 0 | Counter value is not equal to 0 | Count value equals Preset value | None of above | b
|  | MOVE instruction of S7 controllers can not be used to copy which of the following data types? | BYTE | WORD | DOUBLE WORD | BIT | d
|  | In RS Flip Flop of S7, output (Q) is set when | If S = 1 and R = 0 | If S = 0 and R = 1 | If S = 1 and R = 1 | Both option a and c | d
|  | Which coil is used for On Delay Timer? | (SP) | (SD) | (SS) | (SF) | b
|  | Do we need any memory address while using the SAVE instruction | Yes | No | Cannot be said |  | b
|  | What does RLO stands for? | Real Input logic operation | Retentive logical operation | Result of logic operation | None | c
|  | Which of the following is not a comparison instruction? | GE | EQ | LT | MOVE | d
|  | Which timer is switched off when the input is switched off? | On-delay timer | Off-delay timer | Pulse Extended timer | Set storage timer | a

## LANGUAGE
Q. No | Type | Question | A | B | C | D | Correct Answer
|  | Which programming language consumes least memory? | STL | FBD | LAD | All consumes equal. | a
|  | In PLC programming CSF means | continuous set function | control system flow chart | common set fault | none of these | b
|  | In PLC programming all ladder rung can be accomodated in STL | True | False |  |  | a
|  | Programing in Siemens PLC is done using | STL only | CSF only | Ladder only | All above | d
|  | The following is not a language of siemens PLC | STL | FBD | Unix | ladder | c

## PGM BLOCKS
Q. No | Type | Question | A | B | C | D | Correct Answer
|  | Why do you use Data Blocks ? | for storing data. | for calculation purpose. | for storing data and fetching it when ever required and to store the resultant data. | None of the above | c
|  | In Siemens PLC which block is scanned first ? | OB | FB | FC | DB | a
|  | When is Data block scanned ? | In each scanning. | When ever called. | in extreme emergencies. | None of the above | b
|  | For a DB to be used globally, the DB needs to be declared as __________________________. | Instance type | Shared Type | Both of the above | None of these | b
|  | What is the full form of OB? | Object Block | Open Block | Organization Block | None | c
|  | Which is the Cyclic OB? | OB1 | OB2 | OB10 | OB90 | a
|  | Which of the following is/are the Start-up OBs? | OB100 | OB101 | OB102 | All of these | d
|  | DBs assigned to FBs are ____________________________ | essentially shared DBs. | essentially Instance DBs. | either shared DB or instance DB. | neither shared DB or instance DB. | b
|  | During Multiple Instances, which data type has to be specified for Static Variables? | FB<nr> | FC<nr> | Counter | Timer | a
|  | Standard logic blocks for repeatative use can be done by using ___________ in S7 Controllers? | FB | FC | FB & FC | None of above | c
|  | Priority of which block is maximum in S7 controllers | Cyclic Interrupt | Time Interrupt | Time of Day Interrupt | Hardware Interrupt | d
|  | How many types of DBs are there | 2 | 8 | 7 | 9 | a
|  | Which block should be downloaded before downloading the FB? | The DB assigned to it | The SDBs | OB 1 | OB 85 | a
|  | Which type of variables should be declared in multiple instances if we want to run three different motor using the same logic of written in a FB ? | Input variable | Output variable | Static variable | Temporary variable | c
|  | Which type of DB are only related to a specific FBs? | Instance DB | Shared DB | Both a and b option | None | a
|  | Which type of DBs are Global DBs? | Instance DB | Shared DB | Both a and b option | None | b
|  | Multiple Instances programming is possible in case of_______________ | FB | FC | OB | All of the above. | a

## PROGRAMMING
Q. No | Type | Question | A | B | C | D | Correct Answer
|  | If you have to do a HW configuration change, what steps will you follow ? | go to configuration mode ,go on line and change. | make configuration changes off line and reload conguration from PC | make configuration changes off line , put PLC into stop mode and reload conguration from PC and restart. | None of the above | c
|  | Which of the following cannot be given as retentive memory? | Counters | Comparators | Memory Bytes | Timers | b
|  | In S7 PLC retentivity is available for? | Memory bits | Timers | Counters | All of the above | d
|  | Memory Byte assigned to Clock Memory: | Is set by programmer | Pre-activated and can be set by programmer | Cannot be used by programmer | Cannot be set by programmer | a
|  | Which type of program processing method is supported in Siemens PLC | Cyclic | Interrupt | Periodic | All | d
|  | In which Restart all timers, counters and bit memories are reset regardless of whether or not they have been configured as retentive? | Hot Restart | Warm Restart | Cold Restart | All of the above | c
|  | Can Analog Input / Output Word be forced in S7-400? | Yes | No | Cannot be said. |  | a
|  | In which table the status of input and output can be seen | Symbol table | VAT table | Both a and b option |  | b
|  | In S-7 400 PLC Forcing can be done for _______________________ | Digita Inputs only | Digital Output only | Digital I/Os and Analog Inputs only | Both Digital and Analog I/Os | d
|  | If we want to delete all the forcing at a time then which of the follwing should be followed? | Write click on any row then select Delete Force | Select any row as Row Not Effective then Force it | Select any row as Force Value As Comment then Force it | Both option b and c. | a
|  | Sensor break / wire break setting of AI modules can be used for diagnostic interrupt execution. | True | False | Depends on fault | None | a
|  | Unused I/O channels of Analog modules should be __________ | Left Open | Shorted | Deactivated | Selected for voltage signals | c
|  | Input output values are forced in | OB | DB | Variable table | Symbol table | c